## Slide 1: TRANSIENT (ANGLE) STABILITY
Copyright © P. Kundur This material should not be used without the author's consent

## Slide 2: Transient Angle Stability
Description of Transient Stability
An elementary view of TS
Methods of TS analysis
  Time-domain simulation
  Structure of power system model
  Representation faults
Performance of protective relaying
Concept of “electrical centre”
Case studies
Methods of TS enhancement
Major blackouts caused by Transient Instability
  November 9, 1965 Northeast US, Ontario blackout
  March 11, 1999 Brazil blackout
Outline

## Slide 3: What is Transient (Angle) Stability?
The ability of the power system to maintain synchronous operation when subjected to a severe transient disturbance
  faults on transmission circuits, transformers, buses
  loss of generation
  loss of loads
Response involves large excursions of generator rotor angles: influenced by nonlinear power-angle relationship
Stability depends on both the initial operating state of the system and the severity of the disturbance
Post-disturbance steady-state operating conditions usually differ from pre-disturbance conditions

## Slide 4
In large power systems, transient instability may not always occur as "first swing" instability
  could be as a result of superposition of several swing modes causing large excursions of rotor angle beyond the first swing
Study period of interest in transient stability studies is usually limited to 3 to 5 seconds following the disturbance;
  may extend up to about 10 seconds for very large systems with dominant inter-area swing modes
Power system designed and operated to be stable for specified set of contingencies referred to as "normal design contingencies"
  selected on the basis that they have a reasonable probability of occurrence
In the future, probabilistic or risk-based approach may be used

## Slide 5: 1. An Elementary View of Transient Stability
Demonstrate the phenomenon using a very simple system and simple models
System shown in Fig. 13.1
All resistances are neglected
Generator is represented by the classical model
Fig. 13.1 Single machine - infinite bus system

## Slide 6
The generator's electrical power output is
With the stator resistance neglected, Pe represents the air-gap power as well as the terminal power
Fig. 13.2 System representation with generator represented by classical model

## Slide 7: Power-Angle Relationship
Both transmission circuits in-service: Curve 1
  operate at point "a" (Pe = Pm)
One circuit out-of-service: Curve 2
  lower Pmax
  operate at point "b"
  higher reactance  higher  to transmit same power
Fig. 13.3 Power-angle relationship

## Slide 8: Effects of Disturbance
The oscillation of  is superimposed on the synchronous speed 0
Speed deviation
  the generator speed is practically equal to 0, and the per unit (pu) air-gap torque may be considered to be equal to the pu air-gap power
  torque and power are used interchangeably when referring to the swing equation.
Equation of Motion or Swing Equation
where: Pm = mechanical power input (pu)
Pmax = maximum electrical power output (pm)
H = inertia constant (MW-sec/MVA)
 = rotor angle (elec. radians)
t = time (secs)

## Slide 9: Response to a Short Circuit Fault
Illustrate the equal area criterion using the following system:
Examine the impact on stability of different fault clearing times

## Slide 10: Stable Case
Response to a fault cleared in tcl seconds - stable case

## Slide 11: Stable Case cont'd
Pre-disturbance:
both circuits I/S : Pe = Pm, δ = δ0
operating point a
Fault On:
operating point moves from a to b
inertia prevents δ from changing instantaneously
Pm > Pe  rotor accelerates to operating point c
Post Fault:
faulted circuit is tripped, operating point shifts to d
Pe > Pm  rotor decelerates
rotor speed > 0  δ increases
operating point moves from d to e such that A1 = A2
at e, speed = 0, and δ = δ m
Pe > Pm  rotor decelerates; speed below 0
δ decreases and operating point retraces e to d
with no damping, rotor continues to oscillate

## Slide 12: Unstable Case
Response to a fault cleared in tc2 seconds - unstable case

## Slide 13: Unstable Case cont'd
Area A2 above Pm is less than A1
When the operating point reaches e, the kinetic energy gained during the accelerating period has not yet been completely expended
  the speed is still greater than 0 and  continues to increase
Beyond point e, Pe<Pm,  rotor begins to accelerate again
The rotor speed and angle continue to increase leading to loss of synchronism

## Slide 14: Factors Influencing Transient Stability
(a) How heavily the generator is initially loaded.
(b) The generator output during the fault. This depends on the fault location and type.
(c) The fault clearing time.
(d) The post-fault transmission system reactance.
(e) The generator reactance. A lower reactance increases peak power and reduces initial rotor angle.
(f) The generator inertia. The higher the inertia, the slower the rate of change angle. This reduces the kinetic energy gained during fault, i.e. area A1 is reduced.
(g) The generator internal voltage magnitude (El). This depends on the field excitation.
(h) The infinite bus voltage magnitude EB.

## Slide 15: Practical Method of TS Analysis
Practical power systems have complex network structures
Accurate analysis of transient stability requires detailed models for:
  generating unit and controls
  voltage dependent load characteristics
  HVDC converters, FACTs devices, etc.
At present, the most practical available method of transient stability analysis is time domain simulation:
  solution of nonlinear differential equations and algebraic equations
  step-by-step numerical integration techniques
  complimented by efficient techniques for solving non-linear highly sparse algebraic equations

## Slide 16: 2. Numerical Integration Methods
Differential equations to be solved are nonlinear ordinary differential equations with known initial values: x is the state vector of n dependent variables, t is the independent variable (time)
Objective: solve x as a function of t, with the initial values of x and t equal to x0 and t0, respectively.
Methods: Euler's Method Modified Euler's Method Runge-Kutta (R-K) Methods Trapezoidal Rule

## Slide 17: Numerical stability
Depends on propagation of error
Numerically stable if early errors cause no significant errors later
Numerically unstable otherwise
Important to consider numerical stability in the application of numerical integration methods

## Slide 18: Stiffness of Differential Equations
Ratio of largest to smallest time constants or, more precisely, eigenvalues
Increases with modelling detail
Affects numerical stability
Solution using explicit integration methods may "blow up" with stiff systems unless very small time step is used.

## Slide 19: Numerical Stability of Explicit Integration Methods
Explicit Methods
Euler's, Predictor-Corrector, and R-K methods
Dependent variables x at any value of t is computed from a knowledge of the values of x from the previous time steps
  xn+1 for (n+1)th step is calculated explicitly by evaluating f(x,t) with known x
Easy to implement for the solution of a complex set of system state equations
Disadvantage
Not numerically A-stable
  step size limited by small time constants or eigenvalues

## Slide 20: Implicit Integration Methods
Consider the differential equation The solution for x at t=t1=t0+t may be expressed in the integral form as
Implicit methods use interpolation functions for the expression under the integral
Interpolation implies that the functions must pass through the yet unknown points at time t1
Trapezoidal Rule is simplest method

## Slide 21: Trapezoidal Rule
Simplest implicit method; uses linear interpolation
Integral approximated by trapezoids
f(x,t)
f(x0,t0)
f(x1,t1)
t0
t1
t
t
Fig. 13.7

## Slide 22
Trapezoidal rule is given by A general formula giving the value of x at t=tn+1 is
Xn+1 appears on both sides of Equation
  implies that the variable x is computed as a function of its value at the previous time step as well as the current value (which is unknown)
  an implicit equation must be solved
Numerically A-stable : stiffness affects accuracy not stability
Trapezoidal rule is a second order method
Higher order methods difficult to program and less robust

## Slide 23: 3. Simulation of Power System Dynamic Response
Structure of the Power System Model:
Components:
Synchronous generators, and the associated excitation systems and prime movers
Interconnecting transmission network including static loads
Induction and synchronous motor loads
Other devices such as HVDC converters and SVCs
Monitored Information:
Basic stability information
Bus voltages
Line flows
Performance of protective relaying, particularly transmission line protection

## Slide 24
Fig. 13.8 Structure of the complete power system model for transient stability analysis

## Slide 25
Models used must be appropriate for transient stability analysis
  transmission network and machine stator transients are neglected
  dynamics of machine rotors and rotor circuits, excitation systems, prime movers and other devices such as HVDC converters are represented
Equations must be organized in a form suitable for numerical integration
Large set of ordinary differential equations and large sparse algebraic equations
  differential-algebraic initial value problem

## Slide 26: Overall System Equations
Equations for each dynamic device:
where xd = state vector of individual device Id = R and I components of current injection from the device into the network Vd = R and I components of bus voltage
Network equation: where YN = network mode admittance matrix I = node current vector V = node voltage vector

## Slide 27
Overall system equations: comprises a set of first order differentials and a set of algebraic equations where x = state vector of the system V = bus voltage vector I = current injection vector
Time t does not appear explicitly in the above equations
Many approaches for solving these equations characterized by:
  The manner of interface between the differential and algebraic equations: partitioned or simultaneous
  Integration method used
  Method used for solving the algebraic equations:
    Gauss-Seidal method based on admittance matrix
    direct solution using sparsity oriented triangular factorization
    iterative solution using Newton-Raphson method

## Slide 28: Example 13.2
Analyze transient stability including the effects of rotor circuit dynamics and excitation control of the following power plant with four 555 MVA units:
Disturbance: Three phase fault on circuit #2 at F, cleared by tripping the circuit
Fig. E13.6

## Slide 29
Generator parameters:
The four generators of the plant are represented by an equivalent generator whose parameters in per unit on 2220 MVA base are as follows: The above parameters are unsaturated values. The effect of saturation is to be represented assuming the d- and q-axes have similar saturation characteristics based on OCC Excitation system parameters: The generators are equipped with thyristor exciters with AVR and PSS as shown in Fig. 13.12, with parameters as follows: The exciter is assumed to be alternator supplied; therefore EFmax and EFmin are independent of Et Pre-fault system condition in pu on 2220 MVA, 24 kV base: P = 0.9 Q = 0.436 (overexcited) Et = 1.0 28.34 EB = 0.90081 0
Xd=1.81 | Xq=1.76 | Xd=0.30 | Xq=0.65
Xd=0.23 | Xq=0.25 | X1=0.15 | Ra=0.003
To0=8.0s | Tq0=1.0s | Td0=0.03s | Tqo=0.07s
H = 3.5 | K0 = 0 |  | 
''
'
''
'
''
'
'
''
KA= 200 | TR= 0.015s | EFmax= 7.0 | EFmin= -6.4
KSTAB= 9.5 | TW= 1.41s | T1= 0.154s | T2= 0.033s
Vsmax= 0.2 | Vsmin= -0.2 |  | 

## Slide 30
Objective Examine the stability of the system with the following alternative forms of excitation control:
  (i) Manual control, i.e., constant Efd
  (ii) AVR with no PSS
  (iii) AVR with PSS
Consider the following alternative fault clearing times:
  0.07 s
  0.10 s

## Slide 31
Computed using the Gill's version of fourth order R-K integration method with a time step of 0.02 s.
With constant Efd, the system is transiently stable
  however, the level of damping of oscillations is low
With a fast acting AVR and a high exciter ceiling voltage, the first rotor angle swing is significantly reduced
  however, the subsequent swings are negatively damped
  post-fault system small-signal unstable
With the PSS, the rotor oscillations are very well damped without compromising the first swing stability
Case (a): Transient response with the fault clearing time equal to 0.07 s

## Slide 32
Fig. E13.7(a) Rotor angle response with fault cleared in 0.07 s
Fig. E13.7(b) Active power response with fault cleared in 0.07 s

## Slide 33
Fig. E13.7(c) Terminal voltage response with fault cleared in 0.07 s
Fig. E13.7(d) Exciter output voltage response with fault cleared in 0.07 s

## Slide 34
Responses of rotor angle  with the three alternative forms of excitation control are computed
With constant Efd, the generator is first swing unstable
With a fast acting exciter and AVR, the generator maintains first swing stability, but loses synchronism during the second swing
The addition of PSS contributes to the damping of second and subsequent swings
Use of a fast exciter having a high ceiling voltage and equipped with a PSS contributes significantly to the enhancement of the overall system stability!
Case (b): Transient response with the fault clearing time tc equal to 0.1 s

## Slide 35
Fig. E13.8 Rotor angle response with fault cleared in 0.1 s

## Slide 36: 5. Representation of Faults in Stability Studies
Positive-sequence network is represented in detail
Negative- and zero-sequence voltages and currents throughout the system are usually not of interest in stability studies
  unnecessary to simulate the complete negative- and zero-sequence networks in system stability simulations
  effects represented by equivalent impedances (Z2 and Z0) as viewed at the fault point F
Impedances are combined appropriately as the effective fault impedance Zef

## Slide 37: 6. Performance of Protective Relaying
Monitor, detect abnormal conditions, select breakers to be opened, and energize trip circuits
Three requirements: selectivity, speed, and reliability
  distinguish between stable swings and out-of-step
  operate when needed and only when needed
  operate sufficiently fast
  coordinate with other relays
Function of certain relays essential to ensure transient stability
Special relaying may be used to separate systems
Mostly interested in transmission line protection

## Slide 38: Transmission Line Protection
Factors
Type of circuit: single line; parallel line, multi-terminal, magnitude of fault current infeeds, etc.
Function of line, its effect on service continuity, speed with which fault has to be cleared
Coordination and matching requirements
Three basic types:
overcurrent relaying
distance relaying, and
pilot relaying

## Slide 39: (a) Overcurrent Relaying
Simplest and cheapest form of line protection
Two basic forms: instantaneous overcurrent relay and time overcurrent relay
Difficult to apply where coordination, selectivity, and speed are important
  changes to their settings are usually required as system configuration changes
  cannot discriminate between load and fault currents; therefore, when used for phase-fault protection, they are applicable only when the minimum fault current exceeds the full load current
Used principally on subtransmission systems, and radial distribution systems
  faults here usually do not affect system stability so high-speed protection is not required

## Slide 40: (b) Distance Relaying
Responds to a ratio of measured voltage to measured current
Impedance is a measure of distance along the line
Relatively better discrimination and selectivity, by limiting relay operation to a certain range of the impedance
Types
  impedance relay
  reactance relay
  mho relay
  modified mho and impedance relays, and hybrids
Most widely used form for protection of transmission lines
Triggering characteristics shown conveniently on R-X plane

## Slide 41
Fig. 13.28 Distance relay characteristics displayed on a coordinate system with resistance (R) as the abscissa, and reactance (X) as the ordinate

## Slide 42
Three zone approach:
Zone 1 primary protection for protected line
  80% reach and instantaneous
Zone 2 primary protection for protected line
  120% reach and timed (0.3 - 0.5 s)
Zone 3 remote backup protection for adjacent line
  covers next line and timed (2 s)
Fig. 13.29 Distance relay characteristic

## Slide 43: (c) Pilot Relaying Schemes
Use communication channels (pilots) between the terminals of the line that they protect
Determine whether the fault is internal or external to the protected line, and this information is transmitted
For an internal fault, circuit breakers at all terminals of the protected line are tripped; for an external fault the tripping is blocked
Communication medium may be pilot wire (metallic wires), power-line carrier, microwave, or fibre optic

## Slide 44
Each terminal station of the line has:
Underreaching zone 1 phase and ground directional distance relays covering about 75-80% of the line
  trip local breakers instantaneously
Overreaching zone 2 phase and ground directional distance relays covering about 120% of the impedance of the protected line.
  send permissive signal to remote end
  trip local breakers if permissive signal received from remote end
  if apparent Z remains inside relay characteristic for fixed time (typically 0.4 s), local breakers tripped without receiving permissive signal
Fig. 13.30 Permissive overreaching relay
Permissive Overreaching Scheme:

## Slide 45
Fig. 13.31 Relay characteristic at station A
Fig. 13.31 Fault locations F1, F2 and F3

## Slide 46: Fault Clearing Times
Composed of relay time and breaker operating time
  EHV relays: 1-2 cycles
  Circuit breakers: 2-4 cycles
Breaker failure backup protection provided for each breaker on all critical circuits
  if a breaker fails to operate at a local station, trip signals sent to adjacent zone breakers and remote end breakers

## Slide 47
Notes:
(i) For purposes of illustration, 2 cycle breakers have been assumed at A and 3 cycle breakers at B
(ii) Communication time depends on channel medium used. With power line carrier, the time may be longer
 | Local (Bus A) breakers 1 and 2 | Remote (Bus B) breakers 3 and 4
Primary relay time (Fault detection) | 25 ms | 25 ms
Auxiliary relay(s) time | 3 ms | 9 ms
Communication time | - | 17 ms (microwave)
Breaker trip module | 3 ms | 3 ms
Breaker clearing time | 33 ms (2 cycles) | 50 ms (3 cycles)
Total Time | 64 ms | 104 ms
Fault cleared from bus A in 64 milliseconds Fault cleared from bus B in 104 milliseconds |  | 
Fig. 13.34 Typical fault clearing times for a normally cleared fault

## Slide 48
Notes:
Breaker failure timer setting has been assumed to be 90 ms for the 2 cycle breaker 4. This could vary from one application to another. For a 3 cycle oil breaker a typical value is 150 ms
Fig. 13.34 Typical fault clearing times for a stuck breaker fault
 | Local Breaker 5 | Remote breakers 6 and 7 | Local backup breaker 3 | Remote backup breakers 1 and 2
Primary relay time (at bus B) | 25 ms | 25 ms | 25 ms | 25 ms
Auxiliary relay(s) time | 3 ms | 9 ms | 6 ms | 12 ms
Communication channel time | - | 17 ms | - | 17 ms
Breaker failure timer setting | - | - | 90 ms | 90 ms
Breaker tripping module time | 3 ms | 3 ms | 3 ms | 3 ms
Breaker time | 33 ms | 50 ms | 33 ms | 33 ms
Total time | 64 ms | 104 ms | 157 ms | 180 ms
Fault cleared from bus C in 104 milliseconds Fault cleared from bus B in 157 milliseconds Fault cleared from bus A in 180 milliseconds |  |  |  | 
Breaker 4 assumed to be stuck
Breakers 1, 2, 3, 4, and 5 assumed to be 2 cycle air-blast breakers (33 ms)
Breakers 6 and 7 assumed to be 3 cycle oil breakers (50 ms)

## Slide 49: Relaying Quantities During Swings
The performance of protective relaying during electro-mechanical oscillations and out-out-step conditions illustrated by considering the following system:
(a) Schematic diagram
(b) Equivalent circuit
Fig. 13.36 Two machine system
The current I is given by
The voltage at bus C is

## Slide 50
The apparent impedance seen by an impedance relay at C looking towards the line is given by If EA=EB=1.0 pu

## Slide 51
During a swing, the angle changes. Fig. 13.37 shows the locus of ZC as a function of  on an R-X diagram, when EA=EB Note: Origin is assumed to be at C, where the relay is located.
Fig. 13.37 Locus of ZC as a function of , with EA=EB

## Slide 52
When EA and EB are equal, the locus of ZC is seen to be a straight line which is the perpendicular bisector of the total system impedance between A and B, i.e., of the impedance ZT
  the angle formed by lines from A and B to any point on the locus is equal to the corresponding angle 
When =0, the current I is zero and ZC is infinite
When =180°, the voltage at the electrical centre is zero
  the relay at C in effect will see a 3-phase fault at the electrical centre. The electrical centre and impedance centre coincide in this case.
If EA is not equal to EB, the apparent impedance loci are circles, with their centres on extensions of the impedance line AB
When EA>EB, the electrical centre will be above the impedance centre; when EA<EB, the electrical centre will be below the impedance centre. Fig. 13.38 illustrates the shape of the apparent impedance loci for three different values of the ratio EA / EB.

## Slide 53
Fig. 13.38 Loci of ZC with different values of EA/EB

## Slide 54
For generators connected to the main system through a weak transmission system (high external impedance), the electrical centre may appear on the transmission line
When a generator is connected to the main system through a strong transmission system, the electrical centre will be in the step up transformer or possibly within the generator itself
Electrical centres in effect are not fixed points: effective machine reactance and the magnitudes of internal voltages vary during dynamic conditions.
Voltage at the electrical centre drops to zero as  increases to 180° and then increases in magnitude as  increases further until it reaches 360°
  when  reaches 180°, the generator will have slipped a pole; when  reaches the initial value where the swing started, one slip cycle will have been completed.

## Slide 55: Prevention of Transmission Line Tripping During Transient Conditions
Requirements for prevention of tripping during swing conditions fall into two categories:
Prevention of tripping during stable swings, while allowing tripping for unstable transients.
Prevention of tripping during unstable transients, and forcing separation at another point.
Prevention of tripping during stable transients
‘mho’ distance relay characteristic may be too large and have regions into which stable swings may enter
In order to minimize the possibility of tripping during stable swings:
  use of ohm units (blinders)
  composite relays
  shaped relay (lens, peanut, etc.)

## Slide 56
Tripping can occur only for impedance between O1 and O2, and within M
Fig. 13.43 Reduction of mho relay angular range
Fig. 13.44 Shaped Relay

## Slide 57: Out-of-Step Blocking and Tripping Relays
In some cases, it may be desirable to prevent tripping of lines at the natural separation point, and choose the separation point so that:
  load and generation are better balanced on both sides, or
  a critical load is protected, or
  the separation is at a corporate boundary.
In certain instances, it may be desirable to trip faster in order to prevent voltage declining too far.
Principle of out-of-step relaying:
Movement of the apparent impedance under out-of-step conditions is slow compared to its movement when a line fault occurs
  transient swing condition can be detected using two relays having vertical or circular characteristics on an R-X plane
  if time required to cross the two characteristics (OOS2, OOS1) exceeds a specified value, the out-of-step function is initiated

## Slide 58
Fig. 13.45 Out-of-step relaying schemes

## Slide 59
In an out-of-step tripping scheme, local breakers would be tripped. such a scheme could be used to
  speed up tripping to voltage decline
  ensure tripping of a selected line, instead of other more critical circuits
In an out-of-step blocking scheme,
  relays are prevented from initiating tripping of the line monitored, and transfer trip signals are sent to open circuits of a remote location
  objective is to cause system separation at a more preferable location

## Slide 60: 7. Case Study - Transient Stability
The object
  demonstrate transient instability and actions of protective relaying
  show methods of maintaining stability
The system
  2279 buses, 467 generators, and 6581 branches
  the focus is on a plant with 8 nuclear units, with a total capacity of 7000 MW
  all generators and associated controls are modelled in detail
  loads are modelled using voltage-dependent static load model (P=50% l + 50% Z, Q=100% Z)

## Slide 61
Fig. 13.52 Diagram of system in the vicinity of a 7000 MW nuclear power plant

## Slide 62
The Contingency:
Double line-to-ground (LLG) fault occurs on the 500 kV double circuit line at Junction X
Time (ms) | Event
0 | No disturbance
100 | Apply LLG fault at Junction X on circuits 1 and 2
164 | Local end clearing:
 | Open breakers at bus 1 for circuit 1
 | Open breakers at bus 2 for circuit 2
 | This occurs 64 ms after the fault is applied, and this time is computed as the sum of fault detection time (25 ms), auxiliary relay time (6 ms), and the breaker clearing time (33 ms = 2 cycle). At this time, the fault remains connected on the ends of circuits 1 and 2 at Junction X
187 | Remote end clearing:
 | Open breakers at bus 4 for circuit 2
 | Open breakers at bus 3 for circuit 1
 | Clear fault (the line is isolated)
 | This occurs 87 ms after the fault is applied, and the time is calculated as the sum of fault detection time (25 ms), auxiliary relay time (12 ms), communication time (17 ms; microwave), and breaker clearing time (33 ms = 2 cycle)
5000 | Terminate simulation

## Slide 63
Simulation:
A 5 second simulation was performed
G3 is seen to lose synchronism and becomes monotonically unstable
  similar behaviour for the other 7 units of the nuclear plant
As G1 to G8 become unstable, the rest of the system becomes generation deficient
  absolute angles of all machines in the system drift slightly
Fig. 13.53 Rotor angle time response

## Slide 64
Analysis:
How does the system come apart as a result of instability?
Out-of-step protection does not operate on G3
Fig. 13.54 Unit G3 out-of-step protection

## Slide 65
Fig. 13.55 Line protection (circuit 3) at bus 1
Fig. 13.56 Line protection (circuit 3) at bus 7

## Slide 66
Line Protection:
Mho distance relays have zone 1 coverage of about 75% of line length, and zone 2 over-reach of about 125% of line length
Apparent impedance enters the zone 2 relays at bus 1 and enters zone 1 and zone 2 relays at bus 7
  zone 1 relay at bus 7 would trip circuit 3 at bus 7 and send a transfer trip signal to breakers at bus 1 which would then trip circuit 3 at bus 1
  true for the companion 500 kV circuit (#4) which would be tripped in an identical manner
Following the loss of the 500 kV circuits (at approximately 0.8 seconds), the remaining 230 kV circuits would become extremely over-loaded and would be lost through protection actions, thereby completely isolating the unstable plant from the system
Impedance plot shows the impedance swing crosses the circuit at a point about 84% of the line length from bus 1
  represents the electrical centre following the disturbance, and is theoretically where separation occurs

## Slide 67
Bus Voltages:
Fig. 13.57 Voltages at buses 1, 7 and the electrical centre

## Slide 68
Methods of Maintaining Stability:
Reduction of the pre-contingency output of the plant
  costly to bottle energy in the plant
Tripping of 2 generating units (generation rejection) following the disturbance
Fig. 13.58 Unit G3 rotor angle response with and without generation rejection

## Slide 69: 8. Transient Stability Enhancement
Objectives:
Reduce the disturbing influence by minimizing the fault severity and duration
Increase the restoring synchronizing forces
Reduce accelerating torque through control of prime-mover mechanical power
Reduce accelerating torque by applying artificial load

## Slide 70: High-Speed Fault Clearing
Amount of kinetic energy gained by the generators during a fault is directly proportional to the fault duration
  quicker the fault is cleared, the less disturbance it causes
Two-cycle breakers, together with high speed relays and communication, are now widely used in locations where rapid fault clearing is importance
In special circumstances, even faster clearing may be desirable
  development and application of a 1 cycle circuit breaker by Bonneville Power Administration (BPA)
  combined with a rapid response overcurrent type sensor, which anticipates fault magnitude, nearly one-cycle total fault duration is attained
  ultra high speed relaying system for EHV lines based on traveling wave detection
  not in widespread use

## Slide 71: Reduction of Transmission System Reactance
Series inductive reactances of transmission networks are primary determinants of stability limits
  reduction of reactances of various elements of the transmission network improves transient stability by increasing post-fault synchronizing power transfers
Most direct way of achieving this is by reducing the reactances of transmission circuits
  voltage rating, line and conductor configurations, and number of parallel circuits determine the reactances of transmission lines
Additional methods of reducing the network reactances:
  use of transformers with lower leakage reactances
  series capacitor compensation of transmission lines

## Slide 72
Typically, the per unit transformer leakage reactance ranges between 0.1 and 0.15
  for newer transformers, the minimum acceptable leakage reactance that can be achieved within the normal transformer design practices has to be established in consultation with the manufacturer
May be a significant economic advantage in opting for a transformer with the lowest possible reactance
Series capacitors directly offset the line series reactance
  the maximum power transfer capability of a transmission line may be significantly increased by the use of series capacitor banks
  directly translates into enhancement of transient stability, depending on the facilities provided for bypassing the capacitor during faults and for reinsertion after fault clearing
  speed of reinsertion is an important factor in maintaining transient stability; using nonlinear resistors of zinc oxide, the reinsertion is practically instantaneous

## Slide 73
One problem with series capacitor compensation is the possibility of subsynchronous resonance with the nearby turbo alternators
  must be analyzed carefully and appropriate preventive measures taken
Series capacitors have been used to compensate very long overhead lines
  recently, there has been an increasing recognition of the advantages of compensating shorter, but heavily loaded, lines using series capacitors
For transient stability applications, the use of switched series capacitors offers some advantages
  can be switched in upon detection of a fault or power swing, and then removed about half second later
  can be located in a substation where it can serve several lines
  protective relaying is made more complex when series compensation is used, and more so if the series capacitors are switched

## Slide 74: Regulated Shunt Compensation
Can improve system stability by increasing the flow of synchronizing power among interconnected generators (voltage profile control)
Static VAR compensators can be used for this purpose
Fig. 11.60 Performance of a 600 km line with an SVS regulating midpoint voltage

## Slide 75: Regulated Shunt Compensation (cont'd)
Fig. 11.62 Power-angle relationships with regulated compensation at discrete intervals dividing line into n independent sections
n | θ/n (degrees) | 
1 | 44.70 | 1.00
2 | 22.35 | 1.85
3 | 14.90 | 2.74
4 | 11.17 | 3.63
6 | 7.45 | 5.42
8 | 5.59 | 7.22
10 | 4.47 | 9.03

## Slide 76: Dynamic Braking
Uses the concept of applying an artificial electrical load during a transient disturbance to increase the electrical power output of generators and thereby reduce rotor acceleration
One form of dynamic braking involves switching in shunt resistors for about 0.5 seconds following a fault to reduce accelerating power of nearby generators and remove the kinetic energy gained during the fault
  BPA has used such a scheme for enhancing transient stability for faults in the US Pacific Northwest
  brake consists of a 1400 MW, 240 kV resistor made up of 45,000 ft. of 1/2" stainless steel wire strung on 3 towers

## Slide 77
To date, braking resistors have been applied only to hydraulic generating stations remote from load centres
  hydraulic units, in comparison to thermal units, are quite rugged; they can, therefore, withstand the sudden shock of switching in resistors without any adverse effect on the units
If braking resistors are applied to thermal units, the effect on shaft fatigue life must be carefully examined
If the switching duty is found unacceptable, the resistors may have to be switched in three or four steps spread over one full cycle of the lowest torsional mode
Braking resistors used to date are all shunt devices
  series resistors may be used to provide the braking effect
  the energy dissipated is proportional to the generator current rather than voltage
  way of inserting the resistors in series is to install a star-connected three-phase resistor arrangement with a bypass switch in the neutral of the generator- step-up transformer to reduce resistor insulation and switch requirements
  resistor is inserted during a transient disturbance by opening the bypass switch

## Slide 78
Another form of braking resistor application, which enhances system stability for only unbalanced ground faults, consists of a resistor connected permanently between ground and the neutral of the Y connected high voltage winding of the generator step-up transformer
  under balanced conditions no current flows through the neutral resistor
  when line-to-ground or double line-to-ground faults occur, current flows through the neutral connection and the resistive losses act as a dynamic brake
With switched form of braking resistors, the switching times should be based on detailed simulations
  if the resistors remain connected too long, there is a possibility of instability on the "backswing"

## Slide 79: Reactor Switching
Shunt reactors near generators provide a simple and convenient means of improving transient stability
Reactor normally remains connected to the network
Resulting reactive load increases the generator internal voltage and reduces internal rotor angle
Following a fault, the reactor is switched out which further improves stability

## Slide 80: Steam Turbine Fast Valving
Applicable to thermal units to assist in maintaining power system transient stability
Involves rapid closing and opening of steam valves in a prescribed manner to reduce the generator accelerating power, following the recognition of a severe transmission system fault
Use recognized in the early 1930s, but it has not been very widely applied for several reasons
  concerns for any possible adverse effects on the turbine and energy supply system
Since the mid-1960s, utilities have realized that fast valving could be an effective method of improving system stability in some situations
  number of technical papers have been published describing the basic concepts and effects of fast valving
  several utilities have tested and implemented fast valving on some of their units

## Slide 81: Fast Valving Procedures
The main inlet control valves (CV) and the reheat intercept valves (IV) provide a convenient means of controlling the turbine mechanical power
Variety of possibilities exist for the implementation of fast valving schemes
Common scheme: only the intercept valves are rapidly closed and then fully reopened after a short time delay
  since the intercept valves control nearly 70% of the total unit power, this method results in a fairly significant reduction in turbine power
More pronounced temporary reduction in turbine power can be achieved through actuation of both control and intercept valves
Procedure of rapid closing and subsequent full opening of the valves is called momentary fast valving
Due to the post-fault transmission system being much weaker than the pre-fault one, it may be desirable to have the prime-mover power, after being reduced rapidly, return to a level lower than the initial power
  sustained fast valving

## Slide 82: Generator Tripping
Selective tripping of generating units for severe transmission system contingencies has been used as a method of improving system stability for many years
Rejection of generation at an appropriate location in the system reduces power to be transferred over the critical transmission interfaces
Units can be tripped rapidly so this is a very effective means of improving transient stability
Historically, the application confined to hydro plants; now used on fossil and nuclear plants
Many utilities design thermal units so that, after tripping, they continue to run, supplying unit auxiliaries; permits the units to re resynchronized to the system and restored to full load in about 15 to 30 minutes
Major turbine-generator concerns:
  the overspeed resulting from tripping the generator
  thermal stresses due to the rapid load changes
  high levels of shaft torques due to successive disturbances

## Slide 83: Controlled System Separation and Load Shedding
May be used to prevent a major disturbance in one part of an interconnected system from propagating into the rest of the system and causing a severe system breakup
Severe disturbance usually characterized by sudden changes in tie line power
  if detected in time and the information is used to initiate corrective actions, severe system upsets can be averted
Impending instability detected by monitoring one or more of the following: sudden change in power flow through specific transmission circuits, change of bus voltage angle, rate of power change, and circuit breaker auxiliary contacts
Upon detection of the impeding instability, controlled system separation is initiated by opening the appropriate tie lines before cascading outages can occur
In some instances it may be necessary to shed selected loads to balance generation and load in the separated systems
Examples: P/ relay on the tie lines between Ontario Hydro and Manitoba Hydro

## Slide 84: High-Speed Excitation Systems
Significant improvements in transient stability can be achieved through rapid temporary increase of generator excitation
Increase of generator field voltage during a transient disturbance has the effect of increasing the internal voltage of the machine, which in turn increases synchronizing power
High initial response excitation systems with high ceiling voltages are most effective in this regard
  ceiling voltages limited by generator rotor insulation considerations
  for thermal units, limited to about 2.5 to 3.0 times rated-load field voltage
Fast excitation response to terminal voltage variations, required for improvement of transient stability, often leads to degrading the damping of local plant mode oscillations
Supplementary excitation control, commonly referred to as power system stabilizer (PSS) provides a convenient means of damping system oscillations
Use of high initial response excitation systems supplemented with PSS is by far the most effective and economical method of enhancing the overall system stability

## Slide 85: Discontinuous Excitation Control
Properly applied PSS provides damping to both local and inter-area modes of oscillations
Under large signal or transient conditions, the stabilizer generally contributes positively to first swing stability
In the presence of both local and inter-area swing modes, however, the normal stabilizer response can allow the excitation to be reduced after the peak of the first local-mode swing and before the highest composite peak of the swing is reached
Additional improvements in transient stability can be realized by keeping the excitation at ceiling, within terminal voltage constraints, until the highest point of the swing is reached
Discontinuous excitation control scheme referred to as Transient Stability Excitation Control (TSEC) has been developed by Ontario Hydro to achieve the above
  improves transient stability by controlling the generator excitation so that the terminal voltage is maintained near the maximum permissible value of about 1.12 to 1.15 pu over the entire positive swing of the rotor angle

## Slide 86
  uses a signal proportional to change in angle of the generator rotor, in addition to the terminal voltage and rotor speed signals
  angle signal is used only during the transient period of about 2 seconds following a severe disturbance, since it results in oscillatory instability if used continuously
  angle signal prevents premature reversal of field voltage and hence maintains the terminal voltage at a high level during the positive swing of the rotor angle
  excessive terminal voltage is prevented by the terminal voltage limiter
When TSEC used on several generating stations in an area;
  system voltage level in the entire area is raised
  increases power consumed by loads in the entire area, contributing to further improvement in TS

## Slide 87
Fig. 17.7 Block diagram of TSEC scheme
Fig. 17.8 Effect of TSEC on transient stability

## Slide 88: Integrating HVDC Parallel Links
HVDC links are highly controllable. Possible to take advantage of this unique characteristic of the HVDC link to augment the transient stability of the ac system
Parallel application with ac transmission can be effectively used to bypass ac network congestion
Often, provides the best option for using limited right of way
Provides a firewall against cascading outages during major system disturbances
For example, during the August 2003 Blackout of northeast US and eastern Canada,
  Quebec was unaffected
  AC links from New York to New England tripped; however, HVDC links from Quebec continued to supply power to New England
With the present day technology based on self –commutated voltage sourced converters, transient stability augmentation can also be achieved by controlling the HVDC converters so as to provide reactive power and voltage support.

## Slide 89: Examples of HVDC Parallel Links
Pacific HVDC Inter-tie in the US west
  1400 km long 440 kV bipolar HVDC overhead line from Columbia River in Oregon to Los Angeles, California
  Built in the early 1970s, with a capacity of 1,440 MW; upgraded over the years to 3,100 MW
  Has operated successfully for over 30 years in parallel with 500 kV AC transmission
Itaipu HVDC Link in Brazil
  800 km long 600 kV bipolar HVDC overhead line from Foz du Iguacu hydro power plant to the load centre in the city of Sao Paulo
  3,150 MW HVDC link built in the mid 1980s
  Has operated successfully for over 20 years in parallel with 765 kV AC transmission network
Quebec- New England multi-terminal HVDC system
  1500 MW, 1500 km 450 kV bipolar HVDC link built in the early 1990s
  Brings power from James Bay Hydro plants to Boston, Massachusetts area
  Comprises five terminals; normally operates as a three-terminal link

## Slide 90: VSC-Based HVDC Technology
HVDC transmission systems built over the years use converter bridge circuits that rely on natural voltage of the ac system for commutation: “ line-commutated converter technology”
  Results in generation of lower-order harmonics and consumption of reactive power, which in turn call for counter measures
In recent years, “self-commutated voltage-sourced converter (VSC) technology” has been developed and advanced for HVDC transmission application with the following technical benefits:
  Active and reactive power can be controlled independently
  Excellent dynamic response
  Can be connected to very weak ac network
  Harmonic filter requirements are significantly less
  Good “black-start” capability
  Lower overall “footprint” requirements
VSC-based HVDC converters are more expensive and have higher losses
  Depending on the nature of the application, these may not be significant issues

## Slide 91: November 9, 1965 Blackout of Northeast US and Ontario

## Slide 92: November 9, 1965 - Blackout of Northeast US and Canada
Clear day with mild weather; Load levels in the regional normal
Problem began at 5:16 p.m.
Within a few minutes, there was a complete shut down of electric service to
  virtually all of the states of New York, Connecticut, Rhode Island, Massachusetts, Vermont
  parts of New Hampshire, New Jersey and Pennsylvania
  most of Ontario, Canada
Nearly 30 million people were without power for about 13 hours
President Johnson ordered Chairman of Federal Power Commission to conduct an immediate investigation
Developments that followed had a major impact on the industry!

## Slide 93: North American Eastern Interconnected System

## Slide 94: Events that Caused the 1965 Blackout
The initial event was the operation of a backup relay (Zone 3) at Beck GS in Ontario near Niagara Falls
  opened circuit Q29BD, one of five 230 kV circuits connecting Beck GS to load centers in Toronto and Hamilton
Prior to opening of Q29BD, the five circuits were carrying
  1200 MW of Beck generation, and
  500 MW import from Western NY State on Niagara ties
Net import from NY 300 MW
Loading on Q29BD was 361 MW at 248 kV;
The relay setting corresponded to 375 MW

## Slide 95: Events that Caused the 1965 Blackout (cont'd)
Beck

## Slide 96: Events that Caused the 1965 Blackout (cont'd)
Opening of Q29BD resulted in sequential tripping of the remaining four parallel circuits
Power flow reversed to New York
  total change of 1700 MW
Power surge back to Ontario via St. Lawrence ties
  ties tripped by protective relaying
Generators in Western New York and Beck GS lost synchronism, followed by cascading outages
After about 7 seconds from the initial disturbance
  system split into several separate islands
  eventually most generation and load lost; inability of islanded systems to stabilize

## Slide 97: Special Protections Implemented after the 1965 Blackout
P Relays on Niagara Ties
  trip Niagara ties to NY; cross-trip St. Lawrence ties to NY
  in place until mid 1980s
Underfrequency load shedding (UFLS) throughout the interconnected system
  beginning of the use of UFLS by industry

## Slide 98: Formation of Reliability Councils
Northeast Power Coordinating Council (NPCC) formed in January 1966
  to improve coordination in planning and operation among utilities in the region that was blacked out
  first Regional Reliability Council (RRC) in North America
Other eight RRCs formed in the following months
National/North American Electric Reliability Council (NERC) established in 1968

## Slide 99: Reliability Enhancement after the 1965 Blackout
All utilities in North America began to review reliability related policies, practices and procedures
Coordination of activities and information exchange between neighbouring utilities became a priority
Each Regional Council established detailed Reliability criteria and guidelines for member systems
Power system stability studies became an important part of operating studies
  led to the development of improved Transient Stability programs
  exchange of data between utilities
Many of these developments has had an influence on utility practices worldwide

## Slide 100: March 11, 1999 Brazil Blackout

## Slide 101: March 11, 1999 Brazil Blackout
Time: 22:16:00h, System Load: 34,200 MW
Description of the event:
  L-G fault at Bauru substation as a result of lightning causing a bus insulator flashover
  The bus arrangement at Bauru such that the fault is cleared by opening five 440 kV lines
  The power system survived the initial event, but resulted in instability when a short heavily loaded 440 kV line was tripped by zone 3 relay
  Cascading outages of several power plants in Sao Paulo area, followed by loss of HVDC and 750 kV AC links from Itaipu
  Complete system break up: 24,700 MW load loss; several islands remained in operation with a total load of about 10,000 MW
  Restoration of different regions varied from 30 minutes to 4 hours
  Complete blackout of Sao Paulo and Rio de Janeiro areas for about 4 hours

## Slide 102: March 11, 1999 Brazil Blackout (cont'd)
Measures to improve system security:
  Joint Working Group comprising ELECTROBRAS, CEPEL and ONS staff formed
  Organized activities into 8 Task Forces
  Four international experts as advisors
Remedial Actions:
  Power system divided into 5 security zones: regions with major generation and transmission system protected or emergency controls
  All major EHV substations classified into high, medium, low risk categories based on
    impact level to system security of bus faults
    intrinsic reliability level of substation (layout, equipment changes) to reduce risk level
  Improved maintenance of substation equipment and protection/control equipment
  Better training of operators
  Improved restoration plans